## FEEDERs
Gas Turbine Generator GT-7510
Gas Turbine Generator GT-7520
Gas Turbine Generator GT-7530
| VCB-7563 | BUS TIE
Out Going | VCB-7564 | FUTURE ESP
| VCB-7565 | FUTURE WHP
| VCB-7566 | KM-2460 VRU COMPRESSOR (450kW)
| VCB-7567A | TF-7560A 6./0.4kV 4000kVA
| VCB-7567B | TF-7560B 6./0.4kV 4000kVA
| VCB-7568 | FUTURE 3RD STAGE VRU COMPRESSOR (PHASE-2)
| VCB-7569 | FUTURE WHP (PHASE2)

## MV
|  | DEVICE | SIGNAL TYPE |  |  | ECMS I/O MODULE |  |  | ECMS CONT. | IED TO ECMS CONTROLLER |  | ECMS CONTROLLER TO EMCS SERVER | [7 empty] | IMCS to PMCS (Modbus RTU - RS485) |  |  |  |  | PMCS
| Gas Turbine Generator GT-7510 |  | AI | DI | DO | HARDWIRE |  |  |  | Protocol | Telegram Address | Protocol | Type | Telegram Address | [8 empty] | Type | Register / Address | Unit | HMI SCREEN | EVENT | ALARM | TREND
| Generator Protection Relay (GPR) for GTG at MV SWGR |  |  |  |  | Y/N | DI | DO
[14 empty] | IOA1 | IOA2 | IOA3 | IOA
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
GT7510-01 | 24 - Volts per Hertz relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 1 | 0 | 257 | [7 empty] | - | X | X | X | -
GT7510-02 | 27 - Undervoltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 2 | 0 | 513 | [7 empty] | - | X | X | X | -
GT7510-03 | 32 - Directional power relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 3 | 0 | 769 | [7 empty] | - | X | X | X | -
GT7510-04 | 40 - Loss of field relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 4 | 0 | 1025 | [7 empty] | - | X | X | X | -
GT7510-05 | 46 - Reverse-phase or phase-balance current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 5 | 0 | 1281 | [7 empty] | - | X | X | X | -
GT7510-06 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 6 | 0 | 1537 | [7 empty] | - | X | X | X | -
GT7510-07 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 7 | 0 | 1793 | [7 empty] | - | X | X | X | -
GT7510-08 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 8 | 0 | 2049 | [7 empty] | - | X | X | X | -
GT7510-09 | 59 - Overvoltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 9 | 0 | 2305 | [7 empty] | - | X | X | X | -
GT7510-10 | 87 - Differential protective relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 10 | 0 | 2561 | [7 empty] | - | X | X | X | -
GT7510-11 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 11 | 0 | 2817 | [7 empty] | - | X | X | X | -
GT7510-12 | 51V - Voltage-controlled or voltage-restrained overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 12 | 0 | 3073 | [7 empty] | - | X | X | X | -
GT7510-13 | 81 U - Under Frequency relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 13 | 0 | 3329 | [7 empty] | - | X | X | X | -
GT7510-14 | 82 0 - Over Frequency relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 14 | 0 | 3585 | [7 empty] | - | X | X | X | -
GT7510-15 | 47 - Phase sequence voltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 15 | 0 | 3841 | [7 empty] | - | X | X | X | -
GT7510-16 | 74 - Trip Circuit Supervision Alarm | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 16 | 0 | 4097 | [7 empty] | - | X | X | X | -
GT7510-17 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 17 | 0 | 4353 | [7 empty] | kV | X | - | - | X
GT7510-18 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 18 | 0 | 4609 | [7 empty] | kV | X | - | - | X
GT7510-19 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 19 | 0 | 4865 | [7 empty] | kV | X | - | - | X
GT7510-20 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 20 | 0 | 5121 | [7 empty] | kV | X | - | - | X
GT7510-21 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 21 | 0 | 5377 | [7 empty] | kV | X | - | - | X
GT7510-22 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 22 | 0 | 5633 | [7 empty] | kV | X | - | - | X
GT7510-23 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 23 | 0 | 5889 | [7 empty] | Amp | X | - | - | X
GT7510-24 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 24 | 0 | 6145 | [7 empty] | Amp | X | - | - | X
GT7510-25 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 25 | 0 | 6401 | [7 empty] | Amp | X | - | - | X
GT7510-26 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 26 | 0 | 6657 | [7 empty] | - | X | - | - | X
GT7510-27 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 27 | 0 | 6913 | [7 empty] | Hz | X | - | - | X
GT7510-28 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 28 | 0 | 7169 | [7 empty] | kW | X | - | - | X
GT7510-29 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 1 | 29 | 0 | 7425 | [7 empty] | Kvar | X | - | - | X
GT7510-30 | VCB incomer (VCB-7560) at MV SWGR Opened/Closed | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | DP | 1 | 30 | 0 | 7681 | [7 empty] | - | X | X | - | -
GT7510-31 | VCB incomer (VCB-7560) at MV SWGR Trip | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 1 | 31 | 0 | 7937 | [7 empty] | - | X | X | - | -
GT7510-32 | GTG Engine Parameters 1 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 32 | 0 | 8193 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-33 | GTG Engine Parameters 2 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 33 | 0 | 8449 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-34 | GTG Engine Parameters 3 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 34 | 0 | 8705 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-35 | GTG Engine Parameters 4 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 35 | 0 | 8961 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-36 | GTG Engine Parameters 5 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 36 | 0 | 9217 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-37 | GTG Engine Parameters 6 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 37 | 0 | 9473 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-38 | GTG Engine Parameters 7 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 38 | 0 | 9729 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-39 | GTG Engine Parameters 8 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 39 | 0 | 9985 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-40 | GTG Engine Parameters 9 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 40 | 0 | 10241 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-41 | GTG Engine Parameters 10 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 1 | 41 | 0 | 10497 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7510-42 | Synchro command | TBA | - | - | X | N |  |  | X | IEC61850 | TBA | IEC104 | SC | 1 | 42 | 0 | 10753 | [7 empty] | - | X | X | - | -
GT7510-43 | Automatic Synchronize Initiate | TBA | - | - | X | N |  |  | X | IEC61850 | TBA | IEC104 | SC | 1 | 43 | 0 | 11009 | [7 empty] | - | X | X | - | -
GT7520-01 | 24 - Volts per Hertz relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 1 | 0 | 258 | [7 empty] | - | X | X | X | -
GT7520-02 | 27 - Undervoltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 2 | 0 | 514 | [7 empty] | - | X | X | X | -
GT7520-03 | 32 - Directional power relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 3 | 0 | 770 | [7 empty] | - | X | X | X | -
GT7520-04 | 40 - Loss of field relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 4 | 0 | 1026 | [7 empty] | - | X | X | X | -
GT7520-05 | 46 - Reverse-phase or phase-balance current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 5 | 0 | 1282 | [7 empty] | - | X | X | X | -
GT7520-06 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 6 | 0 | 1538 | [7 empty] | - | X | X | X | -
GT7520-07 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 7 | 0 | 1794 | [7 empty] | - | X | X | X | -
GT7520-08 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 8 | 0 | 2050 | [7 empty] | - | X | X | X | -
GT7520-09 | 59 - Overvoltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 9 | 0 | 2306 | [7 empty] | - | X | X | X | -
GT7520-10 | 87 - Differential protective relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 10 | 0 | 2562 | [7 empty] | - | X | X | X | -
GT7520-11 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 11 | 0 | 2818 | [7 empty] | - | X | X | X | -
GT7520-12 | 51V - Voltage-controlled or voltage-restrained overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 12 | 0 | 3074 | [7 empty] | - | X | X | X | -
GT7520-13 | 81 U - Under Frequency relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 13 | 0 | 3330 | [7 empty] | - | X | X | X | -
GT7520-14 | 82 0 - Over Frequency relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 14 | 0 | 3586 | [7 empty] | - | X | X | X | -
GT7520-15 | 47 - Phase sequence voltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 15 | 0 | 3842 | [7 empty] | - | X | X | X | -
GT7520-16 | 74 - Trip Circuit Supervision Alarm | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 16 | 0 | 4098 | [7 empty] | - | X | X | X | -
GT7520-17 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 17 | 0 | 4354 | [7 empty] | kV | X | - | - | X
GT7520-18 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 18 | 0 | 4610 | [7 empty] | kV | X | - | - | X
GT7520-19 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 19 | 0 | 4866 | [7 empty] | kV | X | - | - | X
GT7520-20 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 20 | 0 | 5122 | [7 empty] | kV | X | - | - | X
GT7520-21 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 21 | 0 | 5378 | [7 empty] | kV | X | - | - | X
GT7520-22 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 22 | 0 | 5634 | [7 empty] | kV | X | - | - | X
GT7520-23 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 23 | 0 | 5890 | [7 empty] | Amp | X | - | - | X
GT7520-24 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 24 | 0 | 6146 | [7 empty] | Amp | X | - | - | X
GT7520-25 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 25 | 0 | 6402 | [7 empty] | Amp | X | - | - | X
GT7520-26 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 26 | 0 | 6658 | [7 empty] | - | X | - | - | X
GT7520-27 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 27 | 0 | 6914 | [7 empty] | Hz | X | - | - | X
GT7520-28 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 28 | 0 | 7170 | [7 empty] | kW | X | - | - | X
GT7520-29 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 2 | 29 | 0 | 7426 | [7 empty] | Kvar | X | - | - | X
GT7520-30 | VCB incomer (VCB-7560) at MV SWGR Opened/Closed | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | DP | 2 | 30 | 0 | 7682 | [7 empty] | - | X | X | - | -
GT7520-31 | VCB incomer (VCB-7560) at MV SWGR Trip | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 2 | 31 | 0 | 7938 | [7 empty] | - | X | X | - | -
GT7520-32 | GTG Engine Parameters 1 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 32 | 0 | 8194 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-33 | GTG Engine Parameters 2 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 33 | 0 | 8450 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-34 | GTG Engine Parameters 3 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 34 | 0 | 8706 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-35 | GTG Engine Parameters 4 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 35 | 0 | 8962 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-36 | GTG Engine Parameters 5 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 36 | 0 | 9218 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-37 | GTG Engine Parameters 6 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 37 | 0 | 9474 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-38 | GTG Engine Parameters 7 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 38 | 0 | 9730 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-39 | GTG Engine Parameters 8 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 39 | 0 | 9986 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-40 | GTG Engine Parameters 9 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 40 | 0 | 10242 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-41 | GTG Engine Parameters 10 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 2 | 41 | 0 | 10498 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7520-42 | Synchro command | TBA | - | - | X | N |  |  | X | IEC61850 | TBA | IEC104 | SC | 2 | 42 | 0 | 10754 | [7 empty] | - | X | X | - | -
GT7520-43 | Automatic Synchronize Initiate | TBA | - | - | X | N |  |  | X | IEC61850 | TBA | IEC104 | SC | 2 | 43 | 0 | 11010 | [7 empty] | - | X | X | - | -
GT7530-01 | 24 - Volts per Hertz relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 1 | 0 | 259 | [7 empty] | - | X | X | X | -
GT7530-02 | 27 - Undervoltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 2 | 0 | 515 | [7 empty] | - | X | X | X | -
GT7530-03 | 32 - Directional power relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 3 | 0 | 771 | [7 empty] | - | X | X | X | -
GT7530-04 | 40 - Loss of field relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 4 | 0 | 1027 | [7 empty] | - | X | X | X | -
GT7530-05 | 46 - Reverse-phase or phase-balance current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 5 | 0 | 1283 | [7 empty] | - | X | X | X | -
GT7530-06 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 6 | 0 | 1539 | [7 empty] | - | X | X | X | -
GT7530-07 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 7 | 0 | 1795 | [7 empty] | - | X | X | X | -
GT7530-08 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 8 | 0 | 2051 | [7 empty] | - | X | X | X | -
GT7530-09 | 59 - Overvoltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 9 | 0 | 2307 | [7 empty] | - | X | X | X | -
GT7530-10 | 87 - Differential protective relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 10 | 0 | 2563 | [7 empty] | - | X | X | X | -
GT7530-11 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 11 | 0 | 2819 | [7 empty] | - | X | X | X | -
GT7530-12 | 51V - Voltage-controlled or voltage-restrained overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 12 | 0 | 3075 | [7 empty] | - | X | X | X | -
GT7530-13 | 81 U - Under Frequency relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 13 | 0 | 3331 | [7 empty] | - | X | X | X | -
GT7530-14 | 82 0 - Over Frequency relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 14 | 0 | 3587 | [7 empty] | - | X | X | X | -
GT7530-15 | 47 - Phase sequence voltage relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 15 | 0 | 3843 | [7 empty] | - | X | X | X | -
GT7530-16 | 74 - Trip Circuit Supervision Alarm | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 16 | 0 | 4099 | [7 empty] | - | X | X | X | -
GT7530-17 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 17 | 0 | 4355 | [7 empty] | kV | X | - | - | X
GT7530-18 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 18 | 0 | 4611 | [7 empty] | kV | X | - | - | X
GT7530-19 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 19 | 0 | 4867 | [7 empty] | kV | X | - | - | X
GT7530-20 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 20 | 0 | 5123 | [7 empty] | kV | X | - | - | X
GT7530-21 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 21 | 0 | 5379 | [7 empty] | kV | X | - | - | X
GT7530-22 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 22 | 0 | 5635 | [7 empty] | kV | X | - | - | X
GT7530-23 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 23 | 0 | 5891 | [7 empty] | Amp | X | - | - | X
GT7530-24 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 24 | 0 | 6147 | [7 empty] | Amp | X | - | - | X
GT7530-25 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 25 | 0 | 6403 | [7 empty] | Amp | X | - | - | X
GT7530-26 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 26 | 0 | 6659 | [7 empty] | - | X | - | - | X
GT7530-27 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 27 | 0 | 6915 | [7 empty] | Hz | X | - | - | X
GT7530-28 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 28 | 0 | 7171 | [7 empty] | kW | X | - | - | X
GT7530-29 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 3 | 29 | 0 | 7427 | [7 empty] | Kvar | X | - | - | X
GT7530-30 | VCB incomer (VCB-7560) at MV SWGR Opened/Closed | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | DP | 3 | 30 | 0 | 7683 | [7 empty] | - | X | X | - | -
GT7530-31 | VCB incomer (VCB-7560) at MV SWGR Trip | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 3 | 31 | 0 | 7939 | [7 empty] | - | X | X | - | -
GT7530-32 | GTG Engine Parameters 1 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 32 | 0 | 8195 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-33 | GTG Engine Parameters 2 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 33 | 0 | 8451 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-34 | GTG Engine Parameters 3 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 34 | 0 | 8707 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-35 | GTG Engine Parameters 4 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 35 | 0 | 8963 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-36 | GTG Engine Parameters 5 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 36 | 0 | 9219 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-37 | GTG Engine Parameters 6 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 37 | 0 | 9475 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-38 | GTG Engine Parameters 7 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 38 | 0 | 9731 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-39 | GTG Engine Parameters 8 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 39 | 0 | 9987 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-40 | GTG Engine Parameters 9 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 40 | 0 | 10243 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-41 | GTG Engine Parameters 10 | TBA |  |  |  | N |  |  | X | IEC61850 | TBA | IEC104 | TBA | 3 | 41 | 0 | 10499 | [7 empty] | - | TBA | TBA | TBA | TBA
GT7530-42 | Synchro command | TBA | - | - | X | N |  |  | X | IEC61850 | TBA | IEC104 | SC | 3 | 42 | 0 | 10755 | [7 empty] | - | X | X | - | -
GT7530-43 | Automatic Synchronize Initiate | TBA | - | - | X | N |  |  | X | IEC61850 | TBA | IEC104 | SC | 3 | 43 | 0 | 11011 | [7 empty] | - | X | X | - | -
VCB7564-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 4 | 1 | 0 | 260 | [7 empty] | - | X | X | X | -
VCB7564-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 4 | 2 | 0 | 516 | [7 empty] | - | X | X | X | -
VCB7564-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 4 | 3 | 0 | 772 | [7 empty] | - | X | X | X | -
VCB7564-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 4 | 4 | 0 | 1028 | [7 empty] | - | X | X | X | -
VCB7564-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 4 | 5 | 0 | 1284 | [7 empty] | - | X | X | X | -
VCB7564-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 4 | 6 | 0 | 1540 | [7 empty] | - | X | X | X | -
VCB7564-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 4 | 7 | 0 | 1796 | [7 empty] | - | X | X | X | -
VCB7564-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 8 | 0 | 2052 | [7 empty] | kV | X | - | - | X
VCB7564-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 9 | 0 | 2308 | [7 empty] | kV | X | - | - | X
VCB7564-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 10 | 0 | 2564 | [7 empty] | kV | X | - | - | X
VCB7564-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 11 | 0 | 2820 | [7 empty] | kV | X | - | - | X
VCB7564-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 12 | 0 | 3076 | [7 empty] | kV | X | - | - | X
VCB7564-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 13 | 0 | 3332 | [7 empty] | kV | X | - | - | X
VCB7564-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 14 | 0 | 3588 | [7 empty] | Amp | X | - | - | X
VCB7564-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 15 | 0 | 3844 | [7 empty] | Amp | X | - | - | X
VCB7564-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 16 | 0 | 4100 | [7 empty] | Amp | X | - | - | X
VCB7564-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 17 | 0 | 4356 | [7 empty] | - | X | - | - | X
VCB7564-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 18 | 0 | 4612 | [7 empty] | Hz | X | - | - | X
VCB7564-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 19 | 0 | 4868 | [7 empty] | kW | X | - | - | X
VCB7564-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 4 | 20 | 0 | 5124 | [7 empty] | Kvar | X | - | - | X
VCB7564-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 4 | 21 | 0 | 5380 | [7 empty] | - | X | X | - | -
VCB7564-23 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 4 | 22 | 0 | 5636 | [7 empty] | - | X | X | - | -
VCB7564-24 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 4 | 23 | 0 | 5892 | [7 empty] | - | X | X | - | -
VCB7565-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 5 | 1 | 0 | 261 | [7 empty] | - | X | X | X | -
VCB7565-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 5 | 2 | 0 | 517 | [7 empty] | - | X | X | X | -
VCB7565-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 5 | 3 | 0 | 773 | [7 empty] | - | X | X | X | -
VCB7565-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 5 | 4 | 0 | 1029 | [7 empty] | - | X | X | X | -
VCB7565-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 5 | 5 | 0 | 1285 | [7 empty] | - | X | X | X | -
VCB7565-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 5 | 6 | 0 | 1541 | [7 empty] | - | X | X | X | -
VCB7565-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 5 | 7 | 0 | 1797 | [7 empty] | - | X | X | X | -
VCB7565-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 8 | 0 | 2053 | [7 empty] | kV | X | - | - | X
VCB7565-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 9 | 0 | 2309 | [7 empty] | kV | X | - | - | X
VCB7565-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 10 | 0 | 2565 | [7 empty] | kV | X | - | - | X
VCB7565-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 11 | 0 | 2821 | [7 empty] | kV | X | - | - | X
VCB7565-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 12 | 0 | 3077 | [7 empty] | kV | X | - | - | X
VCB7565-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 13 | 0 | 3333 | [7 empty] | kV | X | - | - | X
VCB7565-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 14 | 0 | 3589 | [7 empty] | Amp | X | - | - | X
VCB7565-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 15 | 0 | 3845 | [7 empty] | Amp | X | - | - | X
VCB7565-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 16 | 0 | 4101 | [7 empty] | Amp | X | - | - | X
VCB7565-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 17 | 0 | 4357 | [7 empty] | - | X | - | - | X
VCB7565-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 18 | 0 | 4613 | [7 empty] | Hz | X | - | - | X
VCB7565-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 19 | 0 | 4869 | [7 empty] | kW | X | - | - | X
VCB7565-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 5 | 20 | 0 | 5125 | [7 empty] | Kvar | X | - | - | X
VCB7565-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 5 | 21 | 0 | 5381 | [7 empty] | - | X | X | - | -
VCB7565-22 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 5 | 22 | 0 | 5637 | [7 empty] | - | X | X | - | -
VCB7565-23 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 5 | 23 | 0 | 5893 | [7 empty] | - | X | X | - | -
VCB7567A-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 6 | 1 | 0 | 262 | [7 empty] | - | X | X | X | -
VCB7567A-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 6 | 2 | 0 | 518 | [7 empty] | - | X | X | X | -
VCB7567A-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 6 | 3 | 0 | 774 | [7 empty] | - | X | X | X | -
VCB7567A-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 6 | 4 | 0 | 1030 | [7 empty] | - | X | X | X | -
VCB7567A-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 6 | 5 | 0 | 1286 | [7 empty] | - | X | X | X | -
VCB7567A-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 6 | 6 | 0 | 1542 | [7 empty] | - | X | X | X | -
VCB7567A-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 6 | 7 | 0 | 1798 | [7 empty] | - | X | X | X | -
VCB7567A-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 8 | 0 | 2054 | [7 empty] | kV | X | - | - | X
VCB7567A-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 9 | 0 | 2310 | [7 empty] | kV | X | - | - | X
VCB7567A-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 10 | 0 | 2566 | [7 empty] | kV | X | - | - | X
VCB7567A-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 11 | 0 | 2822 | [7 empty] | kV | X | - | - | X
VCB7567A-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 12 | 0 | 3078 | [7 empty] | kV | X | - | - | X
VCB7567A-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 13 | 0 | 3334 | [7 empty] | kV | X | - | - | X
VCB7567A-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 14 | 0 | 3590 | [7 empty] | Amp | X | - | - | X
VCB7567A-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 15 | 0 | 3846 | [7 empty] | Amp | X | - | - | X
VCB7567A-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 16 | 0 | 4102 | [7 empty] | Amp | X | - | - | X
VCB7567A-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 17 | 0 | 4358 | [7 empty] | - | X | - | - | X
VCB7567A-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 18 | 0 | 4614 | [7 empty] | Hz | X | - | - | X
VCB7567A-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 19 | 0 | 4870 | [7 empty] | kW | X | - | - | X
VCB7567A-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 6 | 20 | 0 | 5126 | [7 empty] | Kvar | X | - | - | X
VCB7567A-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 6 | 21 | 0 | 5382 | [7 empty] | - | X | X | - | -
VCB7567A-22 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 6 | 22 | 0 | 5638 | [7 empty] | - | X | X | - | -
VCB7567A-23 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 6 | 23 | 0 | 5894 | [7 empty] | - | X | X | - | -
VCB7567B-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 7 | 1 | 0 | 263 | [7 empty] | - | X | X | X | -
VCB7567B-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 7 | 2 | 0 | 519 | [7 empty] | - | X | X | X | -
VCB7567B-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 7 | 3 | 0 | 775 | [7 empty] | - | X | X | X | -
VCB7567B-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 7 | 4 | 0 | 1031 | [7 empty] | - | X | X | X | -
VCB7567B-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 7 | 5 | 0 | 1287 | [7 empty] | - | X | X | X | -
VCB7567B-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 7 | 6 | 0 | 1543 | [7 empty] | - | X | X | X | -
VCB7567B-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 7 | 7 | 0 | 1799 | [7 empty] | - | X | X | X | -
VCB7567B-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 8 | 0 | 2055 | [7 empty] | kV | X | - | - | X
VCB7567B-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 9 | 0 | 2311 | [7 empty] | kV | X | - | - | X
VCB7567B-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 10 | 0 | 2567 | [7 empty] | kV | X | - | - | X
VCB7567B-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 11 | 0 | 2823 | [7 empty] | kV | X | - | - | X
VCB7567B-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 12 | 0 | 3079 | [7 empty] | kV | X | - | - | X
VCB7567B-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 13 | 0 | 3335 | [7 empty] | kV | X | - | - | X
VCB7567B-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 14 | 0 | 3591 | [7 empty] | Amp | X | - | - | X
VCB7567B-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 15 | 0 | 3847 | [7 empty] | Amp | X | - | - | X
VCB7567B-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 16 | 0 | 4103 | [7 empty] | Amp | X | - | - | X
VCB7567B-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 17 | 0 | 4359 | [7 empty] | - | X | - | - | X
VCB7567B-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 18 | 0 | 4615 | [7 empty] | Hz | X | - | - | X
VCB7567B-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 19 | 0 | 4871 | [7 empty] | kW | X | - | - | X
VCB7567B-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 7 | 20 | 0 | 5127 | [7 empty] | Kvar | X | - | - | X
VCB7567B-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 7 | 21 | 0 | 5383 | [7 empty] | - | X | X | - | -
VCB7567B-22 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 7 | 22 | 0 | 5639 | [7 empty] | - | X | X | - | -
VCB7567B-23 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 7 | 23 | 0 | 5895 | [7 empty] | - | X | X | - | -
VCB7569-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 8 | 1 | 0 | 264 | [7 empty] | - | X | X | X | -
VCB7569-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 8 | 2 | 0 | 520 | [7 empty] | - | X | X | X | -
VCB7569-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 8 | 3 | 0 | 776 | [7 empty] | - | X | X | X | -
VCB7569-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 8 | 4 | 0 | 1032 | [7 empty] | - | X | X | X | -
VCB7569-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 8 | 5 | 0 | 1288 | [7 empty] | - | X | X | X | -
VCB7569-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 8 | 6 | 0 | 1544 | [7 empty] | - | X | X | X | -
VCB7569-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 8 | 7 | 0 | 1800 | [7 empty] | - | X | X | X | -
VCB7569-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 8 | 0 | 2056 | [7 empty] | kV | X | - | - | X
VCB7569-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 9 | 0 | 2312 | [7 empty] | kV | X | - | - | X
VCB7569-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 10 | 0 | 2568 | [7 empty] | kV | X | - | - | X
VCB7569-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 11 | 0 | 2824 | [7 empty] | kV | X | - | - | X
VCB7569-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 12 | 0 | 3080 | [7 empty] | kV | X | - | - | X
VCB7569-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 13 | 0 | 3336 | [7 empty] | kV | X | - | - | X
VCB7569-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 14 | 0 | 3592 | [7 empty] | Amp | X | - | - | X
VCB7569-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 15 | 0 | 3848 | [7 empty] | Amp | X | - | - | X
VCB7569-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 16 | 0 | 4104 | [7 empty] | Amp | X | - | - | X
VCB7569-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 17 | 0 | 4360 | [7 empty] | - | X | - | - | X
VCB7569-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 18 | 0 | 4616 | [7 empty] | Hz | X | - | - | X
VCB7569-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 19 | 0 | 4872 | [7 empty] | kW | X | - | - | X
VCB7569-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 8 | 20 | 0 | 5128 | [7 empty] | Kvar | X | - | - | X
VCB7569-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 8 | 21 | 0 | 5384 | [7 empty] | - | X | X | - | -
VCB7569-22 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 8 | 22 | 0 | 5640 | [7 empty] | - | X | X | - | -
VCB7569-23 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 8 | 23 | 0 | 5896 | [7 empty] | - | X | X | - | -
VCB-7566-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 9 | 1 | 0 | 265 | [7 empty] | - | X | X | X | -
VCB-7566-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 9 | 2 | 0 | 521 | [7 empty] | - | X | X | X | -
VCB-7566-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 9 | 3 | 0 | 777 | [7 empty] | - | X | X | X | -
VCB-7566-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 9 | 4 | 0 | 1033 | [7 empty] | - | X | X | X | -
VCB-7566-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 9 | 5 | 0 | 1289 | [7 empty] | - | X | X | X | -
VCB-7566-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 9 | 6 | 0 | 1545 | [7 empty] | - | X | X | X | -
VCB-7566-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 9 | 7 | 0 | 1801 | [7 empty] | - | X | X | X | -
VCB-7566-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 8 | 0 | 2057 | [7 empty] | kV | X | - | - | X
VCB-7566-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 9 | 0 | 2313 | [7 empty] | kV | X | - | - | X
VCB-7566-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 10 | 0 | 2569 | [7 empty] | kV | X | - | - | X
VCB-7566-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 11 | 0 | 2825 | [7 empty] | kV | X | - | - | X
VCB-7566-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 12 | 0 | 3081 | [7 empty] | kV | X | - | - | X
VCB-7566-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 13 | 0 | 3337 | [7 empty] | kV | X | - | - | X
VCB-7566-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 14 | 0 | 3593 | [7 empty] | Amp | X | - | - | X
VCB-7566-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 15 | 0 | 3849 | [7 empty] | Amp | X | - | - | X
VCB-7566-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 16 | 0 | 4105 | [7 empty] | Amp | X | - | - | X
VCB-7566-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 17 | 0 | 4361 | [7 empty] | - | X | - | - | X
VCB-7566-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 18 | 0 | 4617 | [7 empty] | Hz | X | - | - | X
VCB-7566-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 19 | 0 | 4873 | [7 empty] | kW | X | - | - | X
VCB-7566-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 9 | 20 | 0 | 5129 | [7 empty] | Kvar | X | - | - | X
VCB-7566-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 9 | 21 | 0 | 5385 | [7 empty] | - | X | X | - | -
VCB-7566-22 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 9 | 22 | 0 | 5641 | [7 empty] | - | X | X | - | -
VCB-7566-23 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 9 | 23 | 0 | 5897 | [7 empty] | - | X | X | - | -
VCB-7568-01 | 27R - Undervoltage Remanent relay | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 10 | 1 | 0 | 266 | [7 empty] | - | X | X | X | -
VCB-7568-02 | 49 - Thermal overload relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 10 | 2 | 0 | 522 | [7 empty] | - | X | X | X | -
VCB-7568-03 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 10 | 3 | 0 | 778 | [7 empty] | - | X | X | X | -
VCB-7568-04 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 10 | 4 | 0 | 1034 | [7 empty] | - | X | X | X | -
VCB-7568-05 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61854 | TBA | IEC104 | SP | 10 | 5 | 0 | 1290 | [7 empty] | - | X | X | X | -
VCB-7568-06 | 51G - Ground overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61855 | TBA | IEC104 | SP | 10 | 6 | 0 | 1546 | [7 empty] | - | X | X | X | -
VCB-7568-07 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61856 | TBA | IEC104 | SP | 10 | 7 | 0 | 1802 | [7 empty] | - | X | X | X | -
VCB-7568-08 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 8 | 0 | 2058 | [7 empty] | kV | X | - | - | X
VCB-7568-09 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 9 | 0 | 2314 | [7 empty] | kV | X | - | - | X
VCB-7568-10 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 10 | 0 | 2570 | [7 empty] | kV | X | - | - | X
VCB-7568-11 | Line-Line Voltage (L1-L2) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 11 | 0 | 2826 | [7 empty] | kV | X | - | - | X
VCB-7568-12 | Line-Line Voltage (L1-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 12 | 0 | 3082 | [7 empty] | kV | X | - | - | X
VCB-7568-13 | Line-Line Voltage (L2-L3) | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 13 | 0 | 3338 | [7 empty] | kV | X | - | - | X
VCB-7568-14 | Current Phase L1 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 14 | 0 | 3594 | [7 empty] | Amp | X | - | - | X
VCB-7568-15 | Current Phase L2 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 15 | 0 | 3850 | [7 empty] | Amp | X | - | - | X
VCB-7568-16 | Current Phase L3 | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 16 | 0 | 4106 | [7 empty] | Amp | X | - | - | X
VCB-7568-17 | Power Factor | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 17 | 0 | 4362 | [7 empty] | - | X | - | - | X
VCB-7568-18 | Frequency | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 18 | 0 | 4618 | [7 empty] | Hz | X | - | - | X
VCB-7568-19 | Active Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 19 | 0 | 4874 | [7 empty] | kW | X | - | - | X
VCB-7568-20 | Reactive Power | TBA | X | - | - | N |  |  | X | IEC61850 | TBA | IEC104 | MX | 10 | 20 | 0 | 5130 | [7 empty] | Kvar | X | - | - | X
VCB-7568-21 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 10 | 21 | 0 | 5386 | [7 empty] | - | X | X | - | -
VCB-7568-22 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 10 | 22 | 0 | 5642 | [7 empty] | - | X | X | - | -
VCB-7568-23 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 10 | 23 | 0 | 5898 | [7 empty] | - | X | X | - | -
VCB-7563-01 | Bus-tie Protection Relay at MV SWGR | TBA | - | X | - | N |  |  | X | IEC61850 | TBA | IEC104 | SP | 11 | 1 | 0 | 267 | [7 empty] | - | X | X | X | -
VCB-7563-02 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | N |  |  | X | IEC61851 | TBA | IEC104 | SP | 11 | 2 | 0 | 523 | [7 empty] | - | X | X | X | -
VCB-7563-03 | 51 - Time Over-current relay | TBA | - | X | - | N |  |  | X | IEC61852 | TBA | IEC104 | SP | 11 | 3 | 0 | 779 | [7 empty] | - | X | X | X | -
VCB-7563-04 | 51N - Neutral overcurrent relay | TBA | - | X | - | N |  |  | X | IEC61853 | TBA | IEC104 | SP | 11 | 4 | 0 | 1035 | [7 empty] | - | X | X | X | -
VCB-7563-05 | CB Open/Close command | TBA | - | - | X | Y |  | X | - | - | - | IEC104 | DC | 11 | 21 | 0 | 5387 | [7 empty] | - | X | X | - | -
VCB-7563-06 | CB Opened/Closed Position | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | DP | 11 | 22 | 0 | 5643 | [7 empty] | - | X | X | - | -
VCB-7563-07 | CB Trip | TBA | - | X | - | Y | X |  | - | - | - | IEC104 | SP | 11 | 23 | 0 | 5899 | [7 empty] | - | X | X | - | -
EDG (GD-7760) consist of:
Generator Protection Relay for EDG at LV SWGR SB-7760
24 - Volts per Hertz relay
25 - Synch. Check
27 - Undervoltage relay
32P/Q - Directional power relay
40 - Loss of field relay
46 - Reverse-phase or phase-balance current relay
49 - Thermal overload relay
50 - Instantaneuous Over-current relay
51 - Time Over-current relay
51N -Neutral Time Over-current relay
59 - Overvoltage relay
87 - Differential protection
51G - Ground overcurrent
51V - Voltage-controlled or voltage-restrained overcurrent relay
74 - Alarm relay
81 0/U - Frequency relay (over/under-frequency)
Ampere Meter
Volt Meter
Frequency Meter
PF
kW
kVAR
CB Opened
CB Closed
CB Trip
UCP EDG (UCP-7760)
Synch command
Automatic Synchronize Initiate
ESD Trip Command
EDG Engine Parameters 1
EDG Engine Parameters 2
EDG Engine Parameters 3
EDG Engine Parameters 4
EDG Engine Parameters 5
EDG Engine Parameters 6
EDG Engine Parameters 7
EDG Engine Parameters 8
EDG Engine Parameters 9
EDG Engine Parameters 10
Outgoing and Bus-Tie Breaker of MV SWGR SG-7560:
27 - Undervoltage relay
49 - Thermal overload relay
50 - Instantaneuous Over-current relay
50G - Instantaneuous Over-current relay
51 - Time Over-current relay
51G - Ground overcurrent relay
51N - Neutral overcurrent relay
Ampere Meter
Volt Meter
Frequency Meter
PF
kW
kVAR
CB Open command
CB Close command
CB Opened
CB Closed
CB Trip
Temperature & Partial Discharge Online Monitoring System
Motor & Power and Bus Tie Feeder Load Shedding Trip

## LV
LV SWITCHGEAR/MCC (SB-7760)
Protection Relay for Transformer TF-7560A at Incomer
Protection Relay
25 - Synchronizing In Progress
25 - Synchronizing Time Exceeded
25 - Synchronizing Release Close Command
27 - Undervoltage relay
49 - Thermal overload relay
50 - Instantaneuous Overcurrent relay
51 - Time Overcurrent relay
51G - Ground overcurrent relay
ACB Opened
ACB Closed
ACB Trip
Line-Neutral Voltage (L1-G)
Line-Neutral Voltage (L2-G)
Line-Neutral Voltage (L3-G)
Line-Line Voltage (L1-L2)
Line-Line Voltage (L1-L3)
Line-Line Voltage (L2-L3)
Current Phase L1
Current Phase L2
Current Phase L3
Power Factor
Frequency
Active Power
Reactive Power
Temperature Monitoring
Motor & Power and Bus Tie Feeder Load Shedding Trip
ACB Open command
ACB Close command
Protection Relay for Transformer TF-7560B at Incomer
Protection Relay
25 - Synchronizing In Progress
25 - Synchronizing Time Exceeded
25 - Synchronizing Release Close Command
27 - Undervoltage relay
49 - Thermal overload relay
50 - Instantaneuous Overcurrent relay
51 - Time Overcurrent relay
51G - Ground overcurrent relay
ACB Opened
ACB Closed
ACB Trip
Line-Neutral Voltage (L1-G)
Line-Neutral Voltage (L2-G)
Line-Neutral Voltage (L3-G)
Line-Line Voltage (L1-L2)
Line-Line Voltage (L1-L3)
Line-Line Voltage (L2-L3)
Current Phase L1
Current Phase L2
Current Phase L3
Power Factor
Frequency
Active Power
Reactive Power
Temperature Monitoring
Motor & Power and Bus Tie Feeder Load Shedding Trip
ACB Open command
ACB Close command
Protection Relay for JB-7760 at Incomer ACB-7762
Protection Relay
27 - Undervoltage relay
49 - Thermal overload relay
50 - Instantaneuous Overcurrent relay
51 - Time Overcurrent relay
51N - Neutral overcurrent relay
51G - Ground overcurrent relay
Voltage Status/Monitoring/Metering
ACB Opened
ACB Closed
ACB Trip
Line-Neutral Voltage (L1-G)
Line-Neutral Voltage (L2-G)
Line-Neutral Voltage (L3-G)
Line-Line Voltage (L1-L2)
Line-Line Voltage (L1-L3)
Line-Line Voltage (L2-L3)
Current Phase L1
Current Phase L2
Current Phase L3
Power Factor
Frequency
Active Power
Reactive Power
ACB Open command
ACB Close command
LV Bus Tie Breaker ACB-7763
Protection Relay
50 - Instantaneuous Overcurrent relay
51 - Time Overcurrent relay
51N - Neutral overcurrent relay
Incomimg breaker ACB-7762
ACB Opened
ACB Closed
ACB Trip
Incomimg breaker ACB-7762
ACB Opened
ACB Closed
ACB Trip

## IO List Rev. A
[5 empty] | EMCS IO List | [9 empty] | DOCUMENT ID NO: |  |  |  | 9832-ELE-3210006035-LST-1010
[15 empty] | VENDOR'S DOCUMENT NO. |  |  |  | (3)G37014-K4222-B100005
[15 empty] | CHANGE : |  |  |  | ISSUED FOR CONSTRUCTION
[15 empty] | REVISION NUMBER: |  |  |  | 2
| PROJECT NAME: |  |  | PCMS PKT Revamp Amonia
| END USER: |  |  | PT. Pupuk Kalimantan Timur
| CUSTOMER: |  |  | PT. Tripatra Engineers and Constructors
| NO. | LINE UP | Tag Number | FEEDER NAME | SIGNAL | DEVICE | SIGNAL TYPE |  |  | Devices to RTU |  |  | RTU to EMCS | [8 empty] | REMARKS
[7 empty] | AI | DI | DO | Protocol | Type | Register / Telegram Address | Protocol | IOA1 | IOA2 | IOA3 | Unit | HMI SCREEN | EVENT | ALARM | TREND
GT7510-01 | 1 | SG7560 |  | Gas Turbine Generator GT-7510 | 24 - Volts per Hertz relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 1 | 0 | - | X | X | X | -
GT7510-02 | 2 | SG7560 |  | Gas Turbine Generator GT-7510 | 27 - Undervoltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 2 | 0 | - | X | X | X | -
GT7510-03 | 3 | SG7560 |  | Gas Turbine Generator GT-7510 | 32 - Directional power relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 3 | 0 | - | X | X | X | -
GT7510-04 | 4 | SG7560 |  | Gas Turbine Generator GT-7510 | 40 - Loss of field relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 4 | 0 | - | X | X | X | -
GT7510-05 | 5 | SG7560 |  | Gas Turbine Generator GT-7510 | 46 - Reverse-phase or phase-balance current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 5 | 0 | - | X | X | X | -
GT7510-06 | 6 | SG7560 |  | Gas Turbine Generator GT-7510 | 49 - Thermal overload relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 6 | 0 | - | X | X | X | -
GT7510-07 | 7 | SG7560 |  | Gas Turbine Generator GT-7510 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 7 | 0 | - | X | X | X | -
GT7510-08 | 8 | SG7560 |  | Gas Turbine Generator GT-7510 | 51 - Time Over-current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 8 | 0 | - | X | X | X | -
GT7510-09 | 9 | SG7560 |  | Gas Turbine Generator GT-7510 | 59 - Overvoltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 9 | 0 | - | X | X | X | -
GT7510-10 | 10 | SG7560 |  | Gas Turbine Generator GT-7510 | 87 - Differential protective relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 10 | 0 | - | X | X | X | -
GT7510-11 | 11 | SG7560 |  | Gas Turbine Generator GT-7510 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 11 | 0 | - | X | X | X | -
GT7510-12 | 12 | SG7560 |  | Gas Turbine Generator GT-7510 | 51V - Voltage-controlled or voltage-restrained overcurrent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 12 | 0 | - | X | X | X | -
GT7510-13 | 13 | SG7560 |  | Gas Turbine Generator GT-7510 | 81 U - Under Frequency relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 13 | 0 | - | X | X | X | -
GT7510-14 | 14 | SG7560 |  | Gas Turbine Generator GT-7510 | 82 0 - Over Frequency relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 14 | 0 | - | X | X | X | -
GT7510-15 | 15 | SG7560 |  | Gas Turbine Generator GT-7510 | 47 - Phase sequence voltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 15 | 0 | - | X | X | X | -
GT7510-16 | 16 | SG7560 |  | Gas Turbine Generator GT-7510 | 74 - Trip Circuit Supervision Alarm | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 16 | 0 | - | X | X | X | -
GT7510-17 | 17 | SG7560 |  | Gas Turbine Generator GT-7510 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 17 | 0 | kV | X | - | - | X
GT7510-18 | 18 | SG7560 |  | Gas Turbine Generator GT-7510 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 18 | 0 | kV | X | - | - | X
GT7510-19 | 19 | SG7560 |  | Gas Turbine Generator GT-7510 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 19 | 0 | kV | X | - | - | X
GT7510-20 | 20 | SG7560 |  | Gas Turbine Generator GT-7510 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 20 | 0 | kV | X | - | - | X
GT7510-21 | 21 | SG7560 |  | Gas Turbine Generator GT-7510 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 21 | 0 | kV | X | - | - | X
GT7510-22 | 22 | SG7560 |  | Gas Turbine Generator GT-7510 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 22 | 0 | kV | X | - | - | X
GT7510-23 | 23 | SG7560 |  | Gas Turbine Generator GT-7510 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 23 | 0 | Amp | X | - | - | X
GT7510-24 | 24 | SG7560 |  | Gas Turbine Generator GT-7510 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 24 | 0 | Amp | X | - | - | X
GT7510-25 | 25 | SG7560 |  | Gas Turbine Generator GT-7510 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 25 | 0 | Amp | X | - | - | X
GT7510-26 | 26 | SG7560 |  | Gas Turbine Generator GT-7510 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 26 | 0 | - | X | - | - | X
GT7510-27 | 27 | SG7560 |  | Gas Turbine Generator GT-7510 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 27 | 0 | Hz | X | - | - | X
GT7510-28 | 28 | SG7560 |  | Gas Turbine Generator GT-7510 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 28 | 0 | kW | X | - | - | X
GT7510-29 | 29 | SG7560 |  | Gas Turbine Generator GT-7510 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 1 | 29 | 0 | Kvar | X | - | - | X
GT7510-30 | 30 | SG7560 |  | Gas Turbine Generator GT-7510 | VCB incomer (VCB-7560) at MV SWGR Opened/Closed | TBA | - | X | - | IEC61850 | DP | TBA | IEC104 | 1 | 30 | 0 | - | X | X | - | -
GT7510-31 | 31 | SG7560 |  | Gas Turbine Generator GT-7510 | VCB incomer (VCB-7560) at MV SWGR Trip | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 1 | 31 | 0 | - | X | X | - | -
GT7510-32 | 32 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 1 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 32 | 0 | - | TBA | TBA | TBA | TBA
GT7510-33 | 33 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 2 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 33 | 0 | - | TBA | TBA | TBA | TBA
GT7510-34 | 34 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 3 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 34 | 0 | - | TBA | TBA | TBA | TBA
GT7510-35 | 35 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 4 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 35 | 0 | - | TBA | TBA | TBA | TBA
GT7510-36 | 36 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 5 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 36 | 0 | - | TBA | TBA | TBA | TBA
GT7510-37 | 37 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 6 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 37 | 0 | - | TBA | TBA | TBA | TBA
GT7510-38 | 38 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 7 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 38 | 0 | - | TBA | TBA | TBA | TBA
GT7510-39 | 39 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 8 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 39 | 0 | - | TBA | TBA | TBA | TBA
GT7510-40 | 40 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 9 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 40 | 0 | - | TBA | TBA | TBA | TBA
GT7510-41 | 41 | SG7560 |  | Gas Turbine Generator GT-7510 | GTG Engine Parameters 10 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 1 | 41 | 0 | - | TBA | TBA | TBA | TBA
GT7510-42 | 42 | SG7560 |  | Gas Turbine Generator GT-7510 | Synchro command | TBA | - | - | X | IEC61850 | SC | TBA | IEC104 | 1 | 42 | 0 | - | X | X | - | -
GT7510-43 | 43 | SG7560 |  | Gas Turbine Generator GT-7510 | Automatic Synchronize Initiate | TBA | - | - | X | IEC61850 | SC | TBA | IEC104 | 1 | 43 | 0 | - | X | X | - | -
GT7520-01 | 44 | SG7560 |  | Gas Turbine Generator GT-7520 | 24 - Volts per Hertz relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 1 | 0 | - | X | X | X | -
GT7520-02 | 45 | SG7560 |  | Gas Turbine Generator GT-7520 | 27 - Undervoltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 2 | 0 | - | X | X | X | -
GT7520-03 | 46 | SG7560 |  | Gas Turbine Generator GT-7520 | 32 - Directional power relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 3 | 0 | - | X | X | X | -
GT7520-04 | 47 | SG7560 |  | Gas Turbine Generator GT-7520 | 40 - Loss of field relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 4 | 0 | - | X | X | X | -
GT7520-05 | 48 | SG7560 |  | Gas Turbine Generator GT-7520 | 46 - Reverse-phase or phase-balance current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 5 | 0 | - | X | X | X | -
GT7520-06 | 49 | SG7560 |  | Gas Turbine Generator GT-7520 | 49 - Thermal overload relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 6 | 0 | - | X | X | X | -
GT7520-07 | 50 | SG7560 |  | Gas Turbine Generator GT-7520 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 7 | 0 | - | X | X | X | -
GT7520-08 | 51 | SG7560 |  | Gas Turbine Generator GT-7520 | 51 - Time Over-current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 8 | 0 | - | X | X | X | -
GT7520-09 | 52 | SG7560 |  | Gas Turbine Generator GT-7520 | 59 - Overvoltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 9 | 0 | - | X | X | X | -
GT7520-10 | 53 | SG7560 |  | Gas Turbine Generator GT-7520 | 87 - Differential protective relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 10 | 0 | - | X | X | X | -
GT7520-11 | 54 | SG7560 |  | Gas Turbine Generator GT-7520 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 11 | 0 | - | X | X | X | -
GT7520-12 | 55 | SG7560 |  | Gas Turbine Generator GT-7520 | 51V - Voltage-controlled or voltage-restrained overcurrent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 12 | 0 | - | X | X | X | -
GT7520-13 | 56 | SG7560 |  | Gas Turbine Generator GT-7520 | 81 U - Under Frequency relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 13 | 0 | - | X | X | X | -
GT7520-14 | 57 | SG7560 |  | Gas Turbine Generator GT-7520 | 82 0 - Over Frequency relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 14 | 0 | - | X | X | X | -
GT7520-15 | 58 | SG7560 |  | Gas Turbine Generator GT-7520 | 47 - Phase sequence voltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 15 | 0 | - | X | X | X | -
GT7520-16 | 59 | SG7560 |  | Gas Turbine Generator GT-7520 | 74 - Trip Circuit Supervision Alarm | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 16 | 0 | - | X | X | X | -
GT7520-17 | 60 | SG7560 |  | Gas Turbine Generator GT-7520 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 17 | 0 | kV | X | - | - | X
GT7520-18 | 61 | SG7560 |  | Gas Turbine Generator GT-7520 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 18 | 0 | kV | X | - | - | X
GT7520-19 | 62 | SG7560 |  | Gas Turbine Generator GT-7520 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 19 | 0 | kV | X | - | - | X
GT7520-20 | 63 | SG7560 |  | Gas Turbine Generator GT-7520 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 20 | 0 | kV | X | - | - | X
GT7520-21 | 64 | SG7560 |  | Gas Turbine Generator GT-7520 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 21 | 0 | kV | X | - | - | X
GT7520-22 | 65 | SG7560 |  | Gas Turbine Generator GT-7520 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 22 | 0 | kV | X | - | - | X
GT7520-23 | 66 | SG7560 |  | Gas Turbine Generator GT-7520 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 23 | 0 | Amp | X | - | - | X
GT7520-24 | 67 | SG7560 |  | Gas Turbine Generator GT-7520 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 24 | 0 | Amp | X | - | - | X
GT7520-25 | 68 | SG7560 |  | Gas Turbine Generator GT-7520 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 25 | 0 | Amp | X | - | - | X
GT7520-26 | 69 | SG7560 |  | Gas Turbine Generator GT-7520 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 26 | 0 | - | X | - | - | X
GT7520-27 | 70 | SG7560 |  | Gas Turbine Generator GT-7520 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 27 | 0 | Hz | X | - | - | X
GT7520-28 | 71 | SG7560 |  | Gas Turbine Generator GT-7520 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 28 | 0 | kW | X | - | - | X
GT7520-29 | 72 | SG7560 |  | Gas Turbine Generator GT-7520 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 2 | 29 | 0 | Kvar | X | - | - | X
GT7520-30 | 73 | SG7560 |  | Gas Turbine Generator GT-7520 | VCB incomer (VCB-7560) at MV SWGR Opened/Closed | TBA | - | X | - | IEC61850 | DP | TBA | IEC104 | 2 | 30 | 0 | - | X | X | - | -
GT7520-31 | 74 | SG7560 |  | Gas Turbine Generator GT-7520 | VCB incomer (VCB-7560) at MV SWGR Trip | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 2 | 31 | 0 | - | X | X | - | -
GT7520-32 | 75 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 1 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 32 | 0 | - | TBA | TBA | TBA | TBA
GT7520-33 | 76 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 2 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 33 | 0 | - | TBA | TBA | TBA | TBA
GT7520-34 | 77 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 3 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 34 | 0 | - | TBA | TBA | TBA | TBA
GT7520-35 | 78 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 4 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 35 | 0 | - | TBA | TBA | TBA | TBA
GT7520-36 | 79 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 5 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 36 | 0 | - | TBA | TBA | TBA | TBA
GT7520-37 | 80 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 6 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 37 | 0 | - | TBA | TBA | TBA | TBA
GT7520-38 | 81 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 7 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 38 | 0 | - | TBA | TBA | TBA | TBA
GT7520-39 | 82 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 8 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 39 | 0 | - | TBA | TBA | TBA | TBA
GT7520-40 | 83 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 9 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 40 | 0 | - | TBA | TBA | TBA | TBA
GT7520-41 | 84 | SG7560 |  | Gas Turbine Generator GT-7520 | GTG Engine Parameters 10 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 2 | 41 | 0 | - | TBA | TBA | TBA | TBA
GT7520-42 | 85 | SG7560 |  | Gas Turbine Generator GT-7520 | Synchro command | TBA | - | - | X | IEC61850 | SC | TBA | IEC104 | 2 | 42 | 0 | - | X | X | - | -
GT7520-43 | 86 | SG7560 |  | Gas Turbine Generator GT-7520 | Automatic Synchronize Initiate | TBA | - | - | X | IEC61850 | SC | TBA | IEC104 | 2 | 43 | 0 | - | X | X | - | -
GT7530-01 | 87 | SG7560 |  | Gas Turbine Generator GT-7530 | 24 - Volts per Hertz relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 1 | 0 | - | X | X | X | -
GT7530-02 | 88 | SG7560 |  | Gas Turbine Generator GT-7530 | 27 - Undervoltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 2 | 0 | - | X | X | X | -
GT7530-03 | 89 | SG7560 |  | Gas Turbine Generator GT-7530 | 32 - Directional power relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 3 | 0 | - | X | X | X | -
GT7530-04 | 90 | SG7560 |  | Gas Turbine Generator GT-7530 | 40 - Loss of field relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 4 | 0 | - | X | X | X | -
GT7530-05 | 91 | SG7560 |  | Gas Turbine Generator GT-7530 | 46 - Reverse-phase or phase-balance current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 5 | 0 | - | X | X | X | -
GT7530-06 | 92 | SG7560 |  | Gas Turbine Generator GT-7530 | 49 - Thermal overload relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 6 | 0 | - | X | X | X | -
GT7530-07 | 93 | SG7560 |  | Gas Turbine Generator GT-7530 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 7 | 0 | - | X | X | X | -
GT7530-08 | 94 | SG7560 |  | Gas Turbine Generator GT-7530 | 51 - Time Over-current relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 8 | 0 | - | X | X | X | -
GT7530-09 | 95 | SG7560 |  | Gas Turbine Generator GT-7530 | 59 - Overvoltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 9 | 0 | - | X | X | X | -
GT7530-10 | 96 | SG7560 |  | Gas Turbine Generator GT-7530 | 87 - Differential protective relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 10 | 0 | - | X | X | X | -
GT7530-11 | 97 | SG7560 |  | Gas Turbine Generator GT-7530 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 11 | 0 | - | X | X | X | -
GT7530-12 | 98 | SG7560 |  | Gas Turbine Generator GT-7530 | 51V - Voltage-controlled or voltage-restrained overcurrent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 12 | 0 | - | X | X | X | -
GT7530-13 | 99 | SG7560 |  | Gas Turbine Generator GT-7530 | 81 U - Under Frequency relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 13 | 0 | - | X | X | X | -
GT7530-14 | 100 | SG7560 |  | Gas Turbine Generator GT-7530 | 82 0 - Over Frequency relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 14 | 0 | - | X | X | X | -
GT7530-15 | 101 | SG7560 |  | Gas Turbine Generator GT-7530 | 47 - Phase sequence voltage relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 15 | 0 | - | X | X | X | -
GT7530-16 | 102 | SG7560 |  | Gas Turbine Generator GT-7530 | 74 - Trip Circuit Supervision Alarm | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 16 | 0 | - | X | X | X | -
GT7530-17 | 103 | SG7560 |  | Gas Turbine Generator GT-7530 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 17 | 0 | kV | X | - | - | X
GT7530-18 | 104 | SG7560 |  | Gas Turbine Generator GT-7530 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 18 | 0 | kV | X | - | - | X
GT7530-19 | 105 | SG7560 |  | Gas Turbine Generator GT-7530 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 19 | 0 | kV | X | - | - | X
GT7530-20 | 106 | SG7560 |  | Gas Turbine Generator GT-7530 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 20 | 0 | kV | X | - | - | X
GT7530-21 | 107 | SG7560 |  | Gas Turbine Generator GT-7530 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 21 | 0 | kV | X | - | - | X
GT7530-22 | 108 | SG7560 |  | Gas Turbine Generator GT-7530 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 22 | 0 | kV | X | - | - | X
GT7530-23 | 109 | SG7560 |  | Gas Turbine Generator GT-7530 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 23 | 0 | Amp | X | - | - | X
GT7530-24 | 110 | SG7560 |  | Gas Turbine Generator GT-7530 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 24 | 0 | Amp | X | - | - | X
GT7530-25 | 111 | SG7560 |  | Gas Turbine Generator GT-7530 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 25 | 0 | Amp | X | - | - | X
GT7530-26 | 112 | SG7560 |  | Gas Turbine Generator GT-7530 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 26 | 0 | - | X | - | - | X
GT7530-27 | 113 | SG7560 |  | Gas Turbine Generator GT-7530 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 27 | 0 | Hz | X | - | - | X
GT7530-28 | 114 | SG7560 |  | Gas Turbine Generator GT-7530 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 28 | 0 | kW | X | - | - | X
GT7530-29 | 115 | SG7560 |  | Gas Turbine Generator GT-7530 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 3 | 29 | 0 | Kvar | X | - | - | X
GT7530-30 | 116 | SG7560 |  | Gas Turbine Generator GT-7530 | VCB incomer (VCB-7560) at MV SWGR Opened/Closed | TBA | - | X | - | IEC61850 | DP | TBA | IEC104 | 3 | 30 | 0 | - | X | X | - | -
GT7530-31 | 117 | SG7560 |  | Gas Turbine Generator GT-7530 | VCB incomer (VCB-7560) at MV SWGR Trip | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 3 | 31 | 0 | - | X | X | - | -
GT7530-32 | 118 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 1 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 32 | 0 | - | TBA | TBA | TBA | TBA
GT7530-33 | 119 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 2 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 33 | 0 | - | TBA | TBA | TBA | TBA
GT7530-34 | 120 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 3 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 34 | 0 | - | TBA | TBA | TBA | TBA
GT7530-35 | 121 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 4 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 35 | 0 | - | TBA | TBA | TBA | TBA
GT7530-36 | 122 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 5 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 36 | 0 | - | TBA | TBA | TBA | TBA
GT7530-37 | 123 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 6 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 37 | 0 | - | TBA | TBA | TBA | TBA
GT7530-38 | 124 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 7 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 38 | 0 | - | TBA | TBA | TBA | TBA
GT7530-39 | 125 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 8 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 39 | 0 | - | TBA | TBA | TBA | TBA
GT7530-40 | 126 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 9 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 40 | 0 | - | TBA | TBA | TBA | TBA
GT7530-41 | 127 | SG7560 |  | Gas Turbine Generator GT-7530 | GTG Engine Parameters 10 | TBA | 0 | 0 | 0 | IEC61850 | TBA | TBA | IEC104 | 3 | 41 | 0 | - | TBA | TBA | TBA | TBA
GT7530-42 | 128 | SG7560 |  | Gas Turbine Generator GT-7530 | Synchro command | TBA | - | - | X | IEC61850 | SC | TBA | IEC104 | 3 | 42 | 0 | - | X | X | - | -
GT7530-43 | 129 | SG7560 |  | Gas Turbine Generator GT-7530 | Automatic Synchronize Initiate | TBA | - | - | X | IEC61850 | SC | TBA | IEC104 | 3 | 43 | 0 | - | X | X | - | -
VCB7564-01 | 130 | SG7560 |  | VCB-7563 | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 4 | 1 | 0 | - | X | X | X | -
VCB7564-02 | 131 | SG7560 |  | VCB-7563 | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 4 | 2 | 0 | - | X | X | X | -
VCB7564-03 | 132 | SG7560 |  | VCB-7563 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 4 | 3 | 0 | - | X | X | X | -
VCB7564-04 | 133 | SG7560 |  | VCB-7563 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 4 | 4 | 0 | - | X | X | X | -
VCB7564-05 | 134 | SG7560 |  | VCB-7563 | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 4 | 5 | 0 | - | X | X | X | -
VCB7564-06 | 135 | SG7560 |  | VCB-7563 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 4 | 6 | 0 | - | X | X | X | -
VCB7564-07 | 136 | SG7560 |  | VCB-7563 | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 4 | 7 | 0 | - | X | X | X | -
VCB7564-08 | 137 | SG7560 |  | VCB-7563 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 8 | 0 | kV | X | - | - | X
VCB7564-09 | 138 | SG7560 |  | VCB-7563 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 9 | 0 | kV | X | - | - | X
VCB7564-10 | 139 | SG7560 |  | VCB-7563 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 10 | 0 | kV | X | - | - | X
VCB7564-11 | 140 | SG7560 |  | VCB-7563 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 11 | 0 | kV | X | - | - | X
VCB7564-12 | 141 | SG7560 |  | VCB-7563 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 12 | 0 | kV | X | - | - | X
VCB7564-13 | 142 | SG7560 |  | VCB-7563 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 13 | 0 | kV | X | - | - | X
VCB7564-14 | 143 | SG7560 |  | VCB-7563 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 14 | 0 | Amp | X | - | - | X
VCB7564-15 | 144 | SG7560 |  | VCB-7563 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 15 | 0 | Amp | X | - | - | X
VCB7564-16 | 145 | SG7560 |  | VCB-7563 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 16 | 0 | Amp | X | - | - | X
VCB7564-17 | 146 | SG7560 |  | VCB-7563 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 17 | 0 | - | X | - | - | X
VCB7564-18 | 147 | SG7560 |  | VCB-7563 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 18 | 0 | Hz | X | - | - | X
VCB7564-19 | 148 | SG7560 |  | VCB-7563 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 19 | 0 | kW | X | - | - | X
VCB7564-20 | 149 | SG7560 |  | VCB-7563 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 4 | 20 | 0 | Kvar | X | - | - | X
VCB7564-21 | 150 | SG7560 |  | VCB-7563 | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 4 | 21 | 0 | - | X | X | - | -
VCB7564-23 | 151 | SG7560 |  | VCB-7563 | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 4 | 22 | 0 | - | X | X | - | -
VCB7564-24 | 152 | SG7560 |  | VCB-7563 | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 4 | 23 | 0 | - | X | X | - | -
VCB7565-01 | 153 | SG7560 |  | VCB-7564 | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 5 | 1 | 0 | - | X | X | X | -
VCB7565-02 | 154 | SG7560 |  | VCB-7564 | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 5 | 2 | 0 | - | X | X | X | -
VCB7565-03 | 155 | SG7560 |  | VCB-7564 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 5 | 3 | 0 | - | X | X | X | -
VCB7565-04 | 156 | SG7560 |  | VCB-7564 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 5 | 4 | 0 | - | X | X | X | -
VCB7565-05 | 157 | SG7560 |  | VCB-7564 | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 5 | 5 | 0 | - | X | X | X | -
VCB7565-06 | 158 | SG7560 |  | VCB-7564 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 5 | 6 | 0 | - | X | X | X | -
VCB7565-07 | 159 | SG7560 |  | VCB-7564 | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 5 | 7 | 0 | - | X | X | X | -
VCB7565-08 | 160 | SG7560 |  | VCB-7564 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 8 | 0 | kV | X | - | - | X
VCB7565-09 | 161 | SG7560 |  | VCB-7564 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 9 | 0 | kV | X | - | - | X
VCB7565-10 | 162 | SG7560 |  | VCB-7564 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 10 | 0 | kV | X | - | - | X
VCB7565-11 | 163 | SG7560 |  | VCB-7564 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 11 | 0 | kV | X | - | - | X
VCB7565-12 | 164 | SG7560 |  | VCB-7564 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 12 | 0 | kV | X | - | - | X
VCB7565-13 | 165 | SG7560 |  | VCB-7564 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 13 | 0 | kV | X | - | - | X
VCB7565-14 | 166 | SG7560 |  | VCB-7564 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 14 | 0 | Amp | X | - | - | X
VCB7565-15 | 167 | SG7560 |  | VCB-7564 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 15 | 0 | Amp | X | - | - | X
VCB7565-16 | 168 | SG7560 |  | VCB-7564 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 16 | 0 | Amp | X | - | - | X
VCB7565-17 | 169 | SG7560 |  | VCB-7564 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 17 | 0 | - | X | - | - | X
VCB7565-18 | 170 | SG7560 |  | VCB-7564 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 18 | 0 | Hz | X | - | - | X
VCB7565-19 | 171 | SG7560 |  | VCB-7564 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 19 | 0 | kW | X | - | - | X
VCB7565-20 | 172 | SG7560 |  | VCB-7564 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 5 | 20 | 0 | Kvar | X | - | - | X
VCB7565-21 | 173 | SG7560 |  | VCB-7564 | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 5 | 21 | 0 | - | X | X | - | -
VCB7565-22 | 174 | SG7560 |  | VCB-7564 | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 5 | 22 | 0 | - | X | X | - | -
VCB7565-23 | 175 | SG7560 |  | VCB-7564 | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 5 | 23 | 0 | - | X | X | - | -
VCB7567A-01 | 176 | SG7560 |  | VCB-7567A | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 6 | 1 | 0 | - | X | X | X | -
VCB7567A-02 | 177 | SG7560 |  | VCB-7567A | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 6 | 2 | 0 | - | X | X | X | -
VCB7567A-03 | 178 | SG7560 |  | VCB-7567A | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 6 | 3 | 0 | - | X | X | X | -
VCB7567A-04 | 179 | SG7560 |  | VCB-7567A | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 6 | 4 | 0 | - | X | X | X | -
VCB7567A-05 | 180 | SG7560 |  | VCB-7567A | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 6 | 5 | 0 | - | X | X | X | -
VCB7567A-06 | 181 | SG7560 |  | VCB-7567A | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 6 | 6 | 0 | - | X | X | X | -
VCB7567A-07 | 182 | SG7560 |  | VCB-7567A | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 6 | 7 | 0 | - | X | X | X | -
VCB7567A-08 | 183 | SG7560 |  | VCB-7567A | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 8 | 0 | kV | X | - | - | X
VCB7567A-09 | 184 | SG7560 |  | VCB-7567A | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 9 | 0 | kV | X | - | - | X
VCB7567A-10 | 185 | SG7560 |  | VCB-7567A | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 10 | 0 | kV | X | - | - | X
VCB7567A-11 | 186 | SG7560 |  | VCB-7567A | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 11 | 0 | kV | X | - | - | X
VCB7567A-12 | 187 | SG7560 |  | VCB-7567A | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 12 | 0 | kV | X | - | - | X
VCB7567A-13 | 188 | SG7560 |  | VCB-7567A | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 13 | 0 | kV | X | - | - | X
VCB7567A-14 | 189 | SG7560 |  | VCB-7567A | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 14 | 0 | Amp | X | - | - | X
VCB7567A-15 | 190 | SG7560 |  | VCB-7567A | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 15 | 0 | Amp | X | - | - | X
VCB7567A-16 | 191 | SG7560 |  | VCB-7567A | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 16 | 0 | Amp | X | - | - | X
VCB7567A-17 | 192 | SG7560 |  | VCB-7567A | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 17 | 0 | - | X | - | - | X
VCB7567A-18 | 193 | SG7560 |  | VCB-7567A | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 18 | 0 | Hz | X | - | - | X
VCB7567A-19 | 194 | SG7560 |  | VCB-7567A | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 19 | 0 | kW | X | - | - | X
VCB7567A-20 | 195 | SG7560 |  | VCB-7567A | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 6 | 20 | 0 | Kvar | X | - | - | X
VCB7567A-21 | 196 | SG7560 |  | VCB-7567A | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 6 | 21 | 0 | - | X | X | - | -
VCB7567A-22 | 197 | SG7560 |  | VCB-7567A | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 6 | 22 | 0 | - | X | X | - | -
VCB7567A-23 | 198 | SG7560 |  | VCB-7567A | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 6 | 23 | 0 | - | X | X | - | -
VCB7567B-01 | 199 | SG7560 |  | VCB-7567B | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 7 | 1 | 0 | - | X | X | X | -
VCB7567B-02 | 200 | SG7560 |  | VCB-7567B | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 7 | 2 | 0 | - | X | X | X | -
VCB7567B-03 | 201 | SG7560 |  | VCB-7567B | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 7 | 3 | 0 | - | X | X | X | -
VCB7567B-04 | 202 | SG7560 |  | VCB-7567B | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 7 | 4 | 0 | - | X | X | X | -
VCB7567B-05 | 203 | SG7560 |  | VCB-7567B | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 7 | 5 | 0 | - | X | X | X | -
VCB7567B-06 | 204 | SG7560 |  | VCB-7567B | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 7 | 6 | 0 | - | X | X | X | -
VCB7567B-07 | 205 | SG7560 |  | VCB-7567B | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 7 | 7 | 0 | - | X | X | X | -
VCB7567B-08 | 206 | SG7560 |  | VCB-7567B | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 8 | 0 | kV | X | - | - | X
VCB7567B-09 | 207 | SG7560 |  | VCB-7567B | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 9 | 0 | kV | X | - | - | X
VCB7567B-10 | 208 | SG7560 |  | VCB-7567B | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 10 | 0 | kV | X | - | - | X
VCB7567B-11 | 209 | SG7560 |  | VCB-7567B | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 11 | 0 | kV | X | - | - | X
VCB7567B-12 | 210 | SG7560 |  | VCB-7567B | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 12 | 0 | kV | X | - | - | X
VCB7567B-13 | 211 | SG7560 |  | VCB-7567B | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 13 | 0 | kV | X | - | - | X
VCB7567B-14 | 212 | SG7560 |  | VCB-7567B | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 14 | 0 | Amp | X | - | - | X
VCB7567B-15 | 213 | SG7560 |  | VCB-7567B | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 15 | 0 | Amp | X | - | - | X
VCB7567B-16 | 214 | SG7560 |  | VCB-7567B | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 16 | 0 | Amp | X | - | - | X
VCB7567B-17 | 215 | SG7560 |  | VCB-7567B | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 17 | 0 | - | X | - | - | X
VCB7567B-18 | 216 | SG7560 |  | VCB-7567B | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 18 | 0 | Hz | X | - | - | X
VCB7567B-19 | 217 | SG7560 |  | VCB-7567B | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 19 | 0 | kW | X | - | - | X
VCB7567B-20 | 218 | SG7560 |  | VCB-7567B | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 7 | 20 | 0 | Kvar | X | - | - | X
VCB7567B-21 | 219 | SG7560 |  | VCB-7567B | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 7 | 21 | 0 | - | X | X | - | -
VCB7567B-22 | 220 | SG7560 |  | VCB-7567B | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 7 | 22 | 0 | - | X | X | - | -
VCB7567B-23 | 221 | SG7560 |  | VCB-7567B | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 7 | 23 | 0 | - | X | X | - | -
VCB7569-01 | 222 | SG7560 |  | VCB-7569 | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 8 | 1 | 0 | - | X | X | X | -
VCB7569-02 | 223 | SG7560 |  | VCB-7569 | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 8 | 2 | 0 | - | X | X | X | -
VCB7569-03 | 224 | SG7560 |  | VCB-7569 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 8 | 3 | 0 | - | X | X | X | -
VCB7569-04 | 225 | SG7560 |  | VCB-7569 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 8 | 4 | 0 | - | X | X | X | -
VCB7569-05 | 226 | SG7560 |  | VCB-7569 | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 8 | 5 | 0 | - | X | X | X | -
VCB7569-06 | 227 | SG7560 |  | VCB-7569 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 8 | 6 | 0 | - | X | X | X | -
VCB7569-07 | 228 | SG7560 |  | VCB-7569 | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 8 | 7 | 0 | - | X | X | X | -
VCB7569-08 | 229 | SG7560 |  | VCB-7569 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 8 | 0 | kV | X | - | - | X
VCB7569-09 | 230 | SG7560 |  | VCB-7569 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 9 | 0 | kV | X | - | - | X
VCB7569-10 | 231 | SG7560 |  | VCB-7569 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 10 | 0 | kV | X | - | - | X
VCB7569-11 | 232 | SG7560 |  | VCB-7569 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 11 | 0 | kV | X | - | - | X
VCB7569-12 | 233 | SG7560 |  | VCB-7569 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 12 | 0 | kV | X | - | - | X
VCB7569-13 | 234 | SG7560 |  | VCB-7569 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 13 | 0 | kV | X | - | - | X
VCB7569-14 | 235 | SG7560 |  | VCB-7569 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 14 | 0 | Amp | X | - | - | X
VCB7569-15 | 236 | SG7560 |  | VCB-7569 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 15 | 0 | Amp | X | - | - | X
VCB7569-16 | 237 | SG7560 |  | VCB-7569 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 16 | 0 | Amp | X | - | - | X
VCB7569-17 | 238 | SG7560 |  | VCB-7569 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 17 | 0 | - | X | - | - | X
VCB7569-18 | 239 | SG7560 |  | VCB-7569 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 18 | 0 | Hz | X | - | - | X
VCB7569-19 | 240 | SG7560 |  | VCB-7569 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 19 | 0 | kW | X | - | - | X
VCB7569-20 | 241 | SG7560 |  | VCB-7569 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 8 | 20 | 0 | Kvar | X | - | - | X
VCB7569-21 | 242 | SG7560 |  | VCB-7569 | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 8 | 21 | 0 | - | X | X | - | -
VCB7569-22 | 243 | SG7560 |  | VCB-7569 | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 8 | 22 | 0 | - | X | X | - | -
VCB7569-23 | 244 | SG7560 |  | VCB-7569 | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 8 | 23 | 0 | - | X | X | - | -
VCB-7566-01 | 245 | SG7562 |  | 0 | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 9 | 1 | 0 | - | X | X | X | -
VCB-7566-02 | 246 | SG7563 |  | 0 | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 9 | 2 | 0 | - | X | X | X | -
VCB-7566-03 | 247 | SG7564 |  | 0 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 9 | 3 | 0 | - | X | X | X | -
VCB-7566-04 | 248 | SG7565 |  | 0 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 9 | 4 | 0 | - | X | X | X | -
VCB-7566-05 | 249 | SG7566 |  | 0 | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 9 | 5 | 0 | - | X | X | X | -
VCB-7566-06 | 250 | SG7567 |  | 0 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 9 | 6 | 0 | - | X | X | X | -
VCB-7566-07 | 251 | SG7568 |  | 0 | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 9 | 7 | 0 | - | X | X | X | -
VCB-7566-08 | 252 | SG7569 |  | 0 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 8 | 0 | kV | X | - | - | X
VCB-7566-09 | 253 | SG7570 |  | 0 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 9 | 0 | kV | X | - | - | X
VCB-7566-10 | 254 | SG7571 |  | 0 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 10 | 0 | kV | X | - | - | X
VCB-7566-11 | 255 | SG7572 |  | 0 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 11 | 0 | kV | X | - | - | X
VCB-7566-12 | 256 | SG7573 |  | 0 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 12 | 0 | kV | X | - | - | X
VCB-7566-13 | 257 | SG7574 |  | 0 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 13 | 0 | kV | X | - | - | X
VCB-7566-14 | 258 | SG7575 |  | 0 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 14 | 0 | Amp | X | - | - | X
VCB-7566-15 | 259 | SG7576 |  | 0 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 15 | 0 | Amp | X | - | - | X
VCB-7566-16 | 260 | SG7577 |  | 0 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 16 | 0 | Amp | X | - | - | X
VCB-7566-17 | 261 | SG7578 |  | 0 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 17 | 0 | - | X | - | - | X
VCB-7566-18 | 262 | SG7579 |  | 0 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 18 | 0 | Hz | X | - | - | X
VCB-7566-19 | 263 | SG7580 |  | 0 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 19 | 0 | kW | X | - | - | X
VCB-7566-20 | 264 | SG7581 |  | 0 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 9 | 20 | 0 | Kvar | X | - | - | X
VCB-7566-21 | 265 | SG7582 |  | 0 | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 9 | 21 | 0 | - | X | X | - | -
VCB-7566-22 | 266 | SG7583 |  | 0 | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 9 | 22 | 0 | - | X | X | - | -
VCB-7566-23 | 267 | SG7584 |  | 0 | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 9 | 23 | 0 | - | X | X | - | -
VCB-7568-01 | 268 | SG7586 |  | 0 | 27R - Undervoltage Remanent relay | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 10 | 1 | 0 | - | X | X | X | -
VCB-7568-02 | 269 | SG7587 |  | 0 | 49 - Thermal overload relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 10 | 2 | 0 | - | X | X | X | -
VCB-7568-03 | 270 | SG7588 |  | 0 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 10 | 3 | 0 | - | X | X | X | -
VCB-7568-04 | 271 | SG7589 |  | 0 | 50G - Instantaneuous Over-current relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 10 | 4 | 0 | - | X | X | X | -
VCB-7568-05 | 272 | SG7590 |  | 0 | 51 - Time Over-current relay | TBA | - | X | - | IEC61854 | SP | TBA | IEC104 | 10 | 5 | 0 | - | X | X | X | -
VCB-7568-06 | 273 | SG7591 |  | 0 | 51G - Ground overcurrent relay | TBA | - | X | - | IEC61855 | SP | TBA | IEC104 | 10 | 6 | 0 | - | X | X | X | -
VCB-7568-07 | 274 | SG7592 |  | 0 | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61856 | SP | TBA | IEC104 | 10 | 7 | 0 | - | X | X | X | -
VCB-7568-08 | 275 | SG7593 |  | 0 | Line-Neutral Voltage (L1-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 8 | 0 | kV | X | - | - | X
VCB-7568-09 | 276 | SG7594 |  | 0 | Line-Neutral Voltage (L2-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 9 | 0 | kV | X | - | - | X
VCB-7568-10 | 277 | SG7595 |  | 0 | Line-Neutral Voltage (L3-G) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 10 | 0 | kV | X | - | - | X
VCB-7568-11 | 278 | SG7596 |  | 0 | Line-Line Voltage (L1-L2) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 11 | 0 | kV | X | - | - | X
VCB-7568-12 | 279 | SG7597 |  | 0 | Line-Line Voltage (L1-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 12 | 0 | kV | X | - | - | X
VCB-7568-13 | 280 | SG7598 |  | 0 | Line-Line Voltage (L2-L3) | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 13 | 0 | kV | X | - | - | X
VCB-7568-14 | 281 | SG7599 |  | 0 | Current Phase L1 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 14 | 0 | Amp | X | - | - | X
VCB-7568-15 | 282 | SG7600 |  | 0 | Current Phase L2 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 15 | 0 | Amp | X | - | - | X
VCB-7568-16 | 283 | SG7601 |  | 0 | Current Phase L3 | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 16 | 0 | Amp | X | - | - | X
VCB-7568-17 | 284 | SG7602 |  | 0 | Power Factor | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 17 | 0 | - | X | - | - | X
VCB-7568-18 | 285 | SG7603 |  | 0 | Frequency | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 18 | 0 | Hz | X | - | - | X
VCB-7568-19 | 286 | SG7604 |  | 0 | Active Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 19 | 0 | kW | X | - | - | X
VCB-7568-20 | 287 | SG7605 |  | 0 | Reactive Power | TBA | X | - | - | IEC61850 | MX | TBA | IEC104 | 10 | 20 | 0 | Kvar | X | - | - | X
VCB-7568-21 | 288 | SG7606 |  | 0 | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 10 | 21 | 0 | - | X | X | - | -
VCB-7568-22 | 289 | SG7607 |  | 0 | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 10 | 22 | 0 | - | X | X | - | -
VCB-7568-23 | 290 | SG7608 |  | 0 | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 10 | 23 | 0 | - | X | X | - | -
VCB-7563-01 | 291 | SG7610 |  | 0 | Bus-tie Protection Relay at MV SWGR | TBA | - | X | - | IEC61850 | SP | TBA | IEC104 | 11 | 1 | 0 | - | X | X | X | -
VCB-7563-02 | 292 | SG7611 |  | 0 | 50 - Instantaneuous Over-current relay | TBA | - | X | - | IEC61851 | SP | TBA | IEC104 | 11 | 2 | 0 | - | X | X | X | -
VCB-7563-03 | 293 | SG7612 |  | 0 | 51 - Time Over-current relay | TBA | - | X | - | IEC61852 | SP | TBA | IEC104 | 11 | 3 | 0 | - | X | X | X | -
VCB-7563-04 | 294 | SG7613 |  | 0 | 51N - Neutral overcurrent relay | TBA | - | X | - | IEC61853 | SP | TBA | IEC104 | 11 | 4 | 0 | - | X | X | X | -
VCB-7563-05 | 295 | SG7614 |  | 0 | CB Open/Close command | TBA | - | - | X | - | DC | - | IEC104 | 11 | 21 | 0 | - | X | X | - | -
VCB-7563-06 | 296 | SG7615 |  | 0 | CB Opened/Closed Position | TBA | - | X | - | - | DP | - | IEC104 | 11 | 22 | 0 | - | X | X | - | -
VCB-7563-07 | 297 | SG7616 |  | 0 | CB Trip | TBA | - | X | - | - | SP | - | IEC104 | 11 | 23 | 0 | - | X | X | - | -